## Sheet1
| Guide sheet Name | Guide sheet Items | Pass/No Pass/NA
RES MECH
RM10 | RM10 UNDERGROUND | Approved Plans on site (CMC 114.2) | INFORMATION ONLY
Underground duct systems shall be constructed of approved concrete, clay, metal or plastic (CMC 602.1)
Metal ducts shall be protected from corrosion in an approved manner or shall be completely encased in concrete not less than 2 inches thick (CMC 604.2)
|  | Nonmetallic ducts shall be installed in accordance with the manufacturers installation instructions | INFORMATION ONLY
|  | Plastic pipe and fittings shall conform to cell classification 12454-B of ASTM D 1248 or ASTM D 1784 | INFORMATION ONLY
All ducts shall slope to an accessible point of drainage (CMC 604.6)
All ducts shall be made substatially airtight in an approved manner (CMC 602.4)
RM11 | RM11 RADIANT / COILS | Hydronic heating systems shall be installed in accordance with the manufacturers approved installation instructions (AMI) and verified with those documents available on site | INFORMATION ONLY
The equipment, material, and labor neccesary for testing shall be furnished by the person or permit holder that is requesting the inspection (CMC 1201.2.8.1)
The piping shall be tested with water (CMC 1201.2.8.2)
Piping shall be tested with a hydrostatic pressure of at least 50 psig greater than the operating pressure but not less than 100 psig (CMC 1201.2.8.3)
Required tests shall be conducted in the presense of the inspector and piping shall remain exposed to the inspector. Test pressure shall be maintained for at least 30 minutes without indications of a leak (CMC 1201.2.8.3)
All piping, tubing, and fitting materials shall be free of defects and comply with nationally recognized standards approved by the AHJ (CMC 1201.3.1.6
RM20 | RM20 UNDERFLOOR | Suspended equipment min 6in above grade (CMC 904.3.1.2)
Passageway min 22in wide×30in high (CMC 904.11.1)
Passageway max distance 20ft to equipment EXC (CMC 904.11.2)
| DUCTS | Factory-made ducts listed and labeled & installed AMI (CMC 602.3)
Ground clearance min 4in (CMC 604.2 & 3)
18in vertical clearance where needed under duct to prevent cutting off access to crawl space (CMC 604.1A)
Duct joints sealed, taped, or gasketed airtight (CMC 602.4)
Flex duct per listed and labeled (1-1/2in strap every 4ft) (CMC T6-10)
Flex ducts req UL-181B pressure-sensitive tape (CMC 602.4)
| DUCT SUPPORT | Support of ducts to be per manufacturers listed instructions AMI or absent documentation:
• Flex duct - 1-1/2" strap every 4ft with sag a maximum of 1/2" per foot
• Round metal duct - min 1/2" metal straps or 12 gauge wire every 10ft
| Insulation in Unconditioned space (1in fiberglass ≈ R-3) | R-6 min in floor trusses, R-8 elsewhere EXC (CMC 605.0)
RM21 | RM21 RADIANT COILS | Hydronic heating systems shall be installed in accordance with the manufacturers approved installation instructions (AMI) and verified with those documents available on site | INFORMATION ONLY
The equipment, material, and labor neccesary for testing shall be furnished by the person or permit holder that is requesting the inspection (CMC 1201.2.8.1)
The piping shall be tested with water (CMC 1201.2.8.2)
Piping shall be tested with a hydrostatic pressure of at least 50 psig greater than the operating pressure but not less than 100 psig (CMC 1201.2.8.3)
Required tests shall be conducted in the presense of the inspector and piping shall remain exposed to the inspector. Test pressure shall be maintained for at least 30 minutes without indications of a leak (CMC 1201.2.8.3)
All piping, tubing, and fitting materials shall be free of defects and comply with nationally recognized standards approved by the AHJ (CMC 1201.3.1.6
RM30 | RM30 FLUE | Draft hood /barometric damper in same space as WH (CMC 510.12.5)
Terminate min 5ft above draft hood (CMC 510.6.2.1)
Only 1 draft hood (CMC 510.12.3)
Single-wall vents prohibited (NFPA 54-09 & CMC 802.7.4.1)
No single-wall outdoors in cold climate (CMC 802.7.2)
No single-wall in concealed space or attic (CMC 802.7.4.3)
Secure vent connector to draft hood & vent w/screws or other approved means (CMC 802.10.7)
Install vents AMI (most appliances ship w/ GAMA venting tables that include limits for size, length & offsets) (CMC 802.6.1)
Induced-draft (Category I) can be “gravity vent” (CMC 802.1.1)
Vent size >=draft hood size & <=7× draft hood size (CMC 802.6.3.1)
One 60° offset OK, others max 45° EXC (CMC 802.6.1.1)
Provide proper support AMI (CMC 802.6.5)
Insulation shield to min 2in above attic insulation (Manuf)
| Connectors | Connectors short & straight as practical (CMC 802.10.9.1)
Basic max horizontal length 18in per in of diameter (CMC 803.2.2)
Single-wall connector max length 75% of vertical vent (CMC 802.10.9.2)
Type B connector max length 100% of vertical vent (CMC 802.10.9.3)
No single-wall connector through floor, ceiling, or wall (CMC 802.10.14.1)
Slope min 1/4in/ft toward appliance (CMC 802.10.8)
Connect to appliance vent collar w/ screws or AMI (CMC 802.10.7)
| Appliances with Common Venting | 2 draft-hood equipped appliances: common connector >=largest connector + 50% of smaller flue collar outlet size (CMC 802.10.3.4)
Join to common connector as high as possible (CMC 802.10.4.2)
Smaller connector above larger connector when entering vent at different levels EXC (CMC 802.10.4.2)
No natural & forced-vent to common flue (CMC 802.3.4.4)
| B Vent Termination | Must extend above roof (CMC 802.6.2)
Type B or L termination min 5ft height from flue collar (CMC 802.6.2.1)
Min 2ft above vertical surface within 8ft (CMC 802.6.2)
Min 1 ft above roof (CMC 6.2)
Per table for roofs steeper than 6:12 (CMC 802.6.2)
|  | Show direct vent appliance vent termination with clearances specified by manufacturers installation instructions (AMI), submit manufacturers instalation documents, etc. (CMC 802.1.1 & 802.2 & 3) | INFORMATION ONLY
Provide manufacturers listing instructions showing the venting criteria and condesate waste disposal for condensing appliances (CMC 802.4, 802.8, 802.8.5, and 802.9)
Show category of appliance venting, ex: l, ll, lll, lV and verify materials used for venting meet listings as indicated in AMI, Many manufacturers do not allow cellular core ABS or PVC pipe to be used as venting materials (CMC 802.4.3, 802.4, Table 8.1, AMI)
RM31 | RM31 RADIANT COILS | Hydronic heating systems shall be installed in accordance with the manufacturers approved installation instructions (AMI) and verified with those documents available on site | INFORMATION ONLY
The equipment, material, and labor neccesary for testing shall be furnished by the person or permit holder that is requesting the inspection (CMC 1201.2.8.1)
The piping shall be tested with water (CMC 1201.2.8.2)
Piping shall be tested with a hydrostatic pressure of at least 50 psig greater than the operating pressure but not less than 100 psig (CMC 1201.2.8.3)
Required tests shall be conducted in the presense of the inspector and piping shall remain exposed to the inspector. Test pressure shall be maintained for at least 30 minutes without indications of a leak (CMC 1201.2.8.3)
All piping, tubing, and fitting materials shall be free of defects and comply with nationally recognized standards approved by the AHJ (CMC 1201.3.1.6
RM32 | RM32 DUCT (LOW PRESSURE) | Factory-made ducts listed and labeled & installed AMI (CMC 602.3)
All ducts shall be made substatially airtight in an approved manner.
Duct joints sealed, taped, or gasketed airtight (CMC 602.4)
Flex duct per listed and labeled (1-1/2in strap every 4ft) (CMC T6-10)
Flex ducts req UL-181B pressure-sensitive tape (CMC 602.4)
Max 2 stories for vertical riser on factory-made duct (CMC 604.3)
|  | Fireblocking around duct penetrations between floors (LOCAL) | INFORMATION ONLY
|  | Stud cavities prohibited as supply air duct (LOCAL) | INFORMATION ONLY
Stud cavities & joist spaces OK as returns if no condensation [not conveying air from one floor to another] (CMC 602.1)
| DUCT SUPPORT | Support of ducts to be per manufacturers listed instructions AMI or absent documentation: | INFORMATION ONLY
• Flex duct - 1-1/2" strap every 4ft with sag a maximum of 1/2" per foot
• Round metal duct - min 1/2" metal straps or 12 gauge wire every 10ft
| Insulation in Unconditioned space (1in fiberglass ≈ R-3) | R-6 min in floor trusses, R-8 elsewhere EXC (CMC 605.0)
RM33 | RM33 MANUF FIREPLACE | Equipment must be listed and labeled | INFORMATION ONLY
Install listed equipment AMI (CMC 303.1)
Installation instructions to be left on site (CMC 303.1)
|  | Heat source must be capable of maintaining habitable rooms @ 68°F at a point 3ft above floor & 2ft from exterior walls | INFORMATION ONLY
Vented gas fireplaces shall not be installed in bathrooms or bedrooms unless the appliance is listed and the room has the required volume per CMC 701.2 Exc. Direct vent fireplaces (CMC 908.1 & Exc)
Fireplace clearances to be as required by manufacturer (AMI) and/or CMC 908.2B
| DIRECT VENT FIREPLACE | Direct vent fireplaces shall be installed with the vent air intake terminal in the outdoors and in accordance with the manufacturers instructions (AMI) (CMC 908.2D) | INFORMATION ONLY
0-10K Btu/hr min 6in clearance to building openings (CMC 802.8.3)
10K-50K Btu/hr min 9in (CMC 802.8.3)
>50K Btu/hr min 12in (CMC 802.8.3)
12in clearance to finished ground level (CMC 802.8.3)
RM34 | RM34 COMBUSTION AIR | C.A. required for natural draft appliances EXC (CMC 701.1.1)
Mechanical C.A. supply min 0.35cu.ft/minute/kBtu (CMC 701.7)
Appliance interlock required if mechanically supplied C.A. (CMC 701.8.2)
Outside air openings req screens w/ mesh >=1/4in (CMC 701.9B)
No screens allowed on ducts terminating in attic (CMC 701.10)
| INDOOR AIR SOURCE | Min volume of space 50 cu.ft/1 kBtu (CMC 701.2.1)
2 openings in upper & lower 12in (CMC 701.4.1)
ACH = air changes per hour (CMC 701.2.1.1)
Indoor air source alone only OK if infiltration >.40 ACH (CMC 701.2)
If ACH <.40, min volumes for known air infiltration method: + Non fan-assisted appliance (21cu.ft/ACH) per kBtu (CMC 701.2.2)
If ACH <.40, min volumes for known air infiltration method: + Fan-assisted appliance (15cu.ft/ACH) per kBtu (CMC 701.2.2)
Joist/stud space as C.A. duct <=1 fireblock removed (CMC 701.10X)
Openings connecting indoor spaces min 100sq.in each & min 1sq.in/kBtuif on same level, 2sq.in if on different levels (CMC 701.3.1)
| Attic & Crawl-Space Sources | Ventilated attics & crawl spaces considered equivalent to outdoors F53 (CMC Ch7 F7-2 & 3)
Single opening can be to ventilated attic (CMC Ch7 F7-5)
Crawl space only for lower C.A., not upper (CMC 701.10)
2 direct exterior openings min 1sq.in/4kBtu (CMC 701.4.1)
2 vertical ducts min 1sq.in/4kBtu (CMC 701.4.1)
RM35 | RM35 EXHAUST DUCTS | Standard recognized for ventilation and acceptable indoor air quality is ASHRAE 62.2 | INFORMATION ONLY
| WHOLE HOUSE VENTILATION | Bath fans are required in all baths even if there is a window. A kitchen fan is also required. For smaller homes bath and kitchen fans can meet all the whole house ventilation requirements. Larger homes will need a combination of local exhaust and whole house ventilation or your existing forced air system can be modified to meet the requirements. The ventilation requirements can be met either using intermittent or continuous fans. The advantage of using continuous ventilation is that smaller equipment is needed. | INFORMATION ONLY
Natural or mechanical ventilation req’d for all occupied spaces (CMC 402.1)
| NATURAL VENTILATION | Naturally ventilated spaces must be 􀀓 Naturally ventilated spaces must be permanently open to and within 25 ft of operable wall or roof openings to the outdoors, the openable area of which is a minimum of 4% of the net occupiable floor area being naturally ventilated. (The net occupiable floor area is measured from the inside surfaces of the walls, excluding permanently enclosed obstructions such as shafts and columns.) (CMC 402.2)
| MECHANICAL VENTILATION | Mechanical Ventilation - Mechanical outdoor ventilation must be provided for all spaces normally occupied that are not naturally ventilated. The Standards require that a space conditioning system provide outdoor air equal to or exceeding the ventilation rates required for each of the spaces that it serves. (CMC 402.3)
|  | Switching: Continuous systems need to be installed to operate without occupant intervention, but the override must be readily accessible. Any switches controlling a required ventilation system need to be labeled as to function unless it is obvious such as a bath fan switch. | INFORMATION ONLY
|  | Ducting: 3” flex duct is not permitted. No more than 5 feet of 3” smooth duct for fans up to 50cfm is allowable. 4” flex duct can be used for 70 feet for up to 50cfm fans, 35ft for 80cfm fans, not permitted | 2008 California Building Efficiency Standards
Whole‐Building or Continuous Ventilation Fans shall be rated for sound at a maximum of 1.0 Sone
Whole house or continuous ventilation fans max 1.0 sone Exc (ASHRAE 62.2 7.2.1)
| Note: | Sone = unit of loudness. Normal talking at 3 feet away ranges from 1 to 4 sones. | INFORMATION ONLY
| BATHROOM EXHAUST | Exhaust fans are required in all bathrooms, even if an operable window is installed. Exhaust fans and lighting shall have separate control switches (even if a combination unit is installed). The exhaust fan may need to be supplied by a GFI protected circuit based on the manufacturer’s requirements. (2008 California Energy Efficiency Standards Section 150)
Envionmental air ducts shall be substatially airtight, ducts under pressure shall not pass through other ducts or plenums. Exhaust ducts shall terminate outside the building and be equiped with back-draft dampers (CMC 504.1)
Envionmental air ducts shall terminate a minimum of three (3) feet from property line and three (3) feet from openings into the building (CMC 504.5)
|  | Exhaust fans at shower shall be listed for wet location and shall be GFCI protected. | INFORMATION ONLY
Toilet rooms and kitchen shall provide minimum exhaust rate per CMC Table 4-4.
Mechanical ventilation shall be provided when natural ventilation is not permitted. Ventilation rates shall be designed per CMC 403.1.1 thru 403.5
Bathroom exhaust fan shall comply with requirement of Cal Green code section 4.506.1
Factory made air ducts shall comply with reference standard Chapter 17. Support of ducts, installer shall provide the manufacture’s field fabrication and installation instruction. (CMC 604.5)
Fan shall meet ASHRAE standard 62.2. A maximum of 3 sone rating is required.
Whole‐Building or Continuous Ventilation Fans shall be rated for sound at a maximum of 1.0 Sone (ASHRAE standard 62.2)
| KITCHENS | Freestanding ranges must be household type: not commercial | INFORMATION ONLY
Mechanical exhaust req'd in each kitchen (ASHRAE 62.2 5.1)
Kitchen exhaust min 100 cfm intermittent or 5 ACH continuous (ASHRAE 62.2 T5.1 & T5.2)
Vented range hood req'd if 100 cfm is < 5 kitchen ACH (ASHRAE 62.2 T5.1)
Whole‐Building or Continuous Ventilation Fans shall be rated for sound at a maximum of 1.0 Sone (ASHRAE standard 62.2)
Verticle clearance to combustibles min 30 in EXC: lesser clearance AMI or 24 in OK w/metal hood or metal over millboard (CMC 916.1)
Side clearance to combustibles per AMI or 6 in sides and rear for unlisted appliances (CMC 916.1)
Hood for open top broilers are required and must extend as wide as broiler (CMC 920.3)
Hood for open top broilers must be ducted to outdoors & have backdraft damper (CMC 504.1)
household range hoods must be routed outdoors EXC: ductless (recirculating hoods ok if other mechanical exhaust is provided for the kitchen area (CMC 504.5 & 303.1 & 2008 California Energy Efficiency Standards )
|  | The ducting for the exhaust fan shall be sized according to ASHRAE Standard 62.2, Table 7.1. Flex duct shall not be used in range hood. | INFORMATION ONLY
| LAUNDRY SPACE | Conventional clothes dryers shall be vented to the outdoors. Electric condensing dryers are not vented and shall be plumbed to a drain according to the manufacturer’s instructions. | INFORMATION ONLY
Connectors not concealed & max 6ft (CMC 504.3.2.1X)
Duct smooth metal, no screws in air flow (CMC 504.3.2.1)
Duct min 4in diameter (CMC 504.3.2)
UMC: Max length 14ft minus 2ft each 90° turn more than 2 (CMC 504.3.2.2)
End outside in backdraft damper & no screens (CMC 504.3.1)
Min 3ft from other building openings (LOCAL)
Closet requires make-up air opening [min 100sq.in IRC] per AMI (NFPA 54:10.4.3.1 & CMC 905.3A)
| CAL GREEN | Exhaust fans which terminate outside the building are provided in every bathroom per CGC 4.506.1.
Installed whole house exhaust fans will have insulated louvers or covers with a minimum insulation value of 4.2, which will close when the fan is off.
The duct system has been sized, designed and provided with equipment in accordance with one of the following:
1. Heat Loss/Heat Gain values in accordance with ACCA Manual J or equivalent;
2. Size the duct system in accordance to ACCA 29-D, Manual D or equivalent;
3. Select heating and cooling equipment in accordance with ACCA 36-S, Manual S.
HVAC system installers are trained and certified in the proper installation of HVAC systems per CGC 702.1.
RM38 | RM38 FRAME O.K. | OK to cover pending Bldg/Elec/Plbg | INFORMATION ONLY
RM40 | RM40 EQUIPMENT | Provide all equipment/appliance manufacturers listed installation documentation at time of inspections to verify compliance with installation per AMI. | INFORMATION ONLY
|  | Verify materials specified for venting/exhaust comply with AMI and/or CMC | INFORMATION ONLY
|  | Verify that any and all required clearances to combustibles and as required for service comply with the manufacturers listed clearances of equipment, appliances, and AMI of materials installed. | INFORMATION ONLY
RM41 | RM41 ENERGY FORMS/CALGREEN | 2008 Energy Efficiency Standards setback thermostat installed RCM 4.5.1
Provide original copies of correctly filled out CF-6R Installation Certificate forms for the field inspector at or prior to the final inspection.
Required Energy Efficiency Standards Compliance Forms (2008 EES):
• Domestic Hot Water (DHW) CF-6R-MECH-01
• Solar Domestic Hot Water Systems (SDHW) CF-6R-MECH-02
• Pool and Spa Heating Systems CF-6R-MECH-03
• Space Conditioning Systems, Ducts and Fans CF-6R-MECH-04
• Indoor Air Quality and Mechanical Ventilation CF-6R-MECH-05
• Provide completed HERS Certificates of Field Verification and Diagnostic Testing as required by the
approved Title 24 Report or per the requirements outlined under the prescriptive methods in the 2008
Residential Compliance Manual.
Provide Pex / CPVC water piping certification that meet the flushing and tagging procedures listed in CPC §604
Collect required Special Inspection Final Reports
| AIR CONDTIONING | Insulation protected from physical damage and UV resistant coating (LOCAL)
|  | Manufacturer’s installation instructions for the AC system shall be left on site for the inspector | INFORMATION ONLY
Condensing unit must be on a pad at least 3 inches above grade. (LOCAL)
|  | Line sets properly insulated, supported and fire wall penetrations adequately sealed. | INFORMATION ONLY
|  | AC condensing units designed to be anchored in place by manufacturer shall be so anchored. | INFORMATION ONLY
|  | Manufacturer required clearances shall be maintained. | INFORMATION ONLY
|  | A/C compressor(s) Shall be indicated and located per approved site plan. | INFORMATION ONLY
Disconnect shall be readily accessible and not more than 6’-7” above grade. (do not install disconnect behind unit.) CEC §440.14, Identification of equipment: For more than one unit permanent identification on A/C unit disconnect. CMC §304.5
Secure A/C unit to platform. CMC §303.6
Verify that circuit breaker &/or fuse are sized per name plate. CEC §440.4 (B)
Verify that an accessible electrical receptacle is installed at the same level and within 25’ of the A/C unit. The outlet shall not be connected to the load side of the A/C disconnect. CEC §210.63
Refrigerant suction line with ¾” insulation, 1” if over 2” dia. ENR&150(j)
Insulation protected from physical damage and UV resistant coating ENR $150(m)
RM86 | RM86 FINAL MECHANICAL | OK per Mechanical to occupy pending Bldg/Elec/Plbg